## Slide 1: Example of using solar pumping design software:
COMPASS

## Slide 2
Before starting, click the settings tab and click ‘show additional inputs’ under expert mode
Presentation Screen when opening COMPASS:

## Slide 3: Presentation Screen when opening COMPASS:
Click on either Submersible or Surface depending on the kind of scheme
Useful webinars introducing COMPASS

## Slide 4: Example for Submersible pump
Select your location by introducing
Country and City OR GPS point
Leave the system to suggest the best performing angles for solar panel installation
Motor cable length =Typically pump installation depth+20 meters. Make your best guess in case you don’t know yet pump depth, as Motor cable length has little influence
Lost due to panels being covered with dust. If in dusty environment with little possibility to clean panels regularly, dirt lost=10%. Otherwise leave it at 5%.
Only relevant if you are pumping hot water, as it wont refrigerate the pump properly. Otherwise, leave it at 25C
If you don’t know Total Dynamic Head of your system, tick on Pipe Length and fill the information to the best of your knowledge (see next slide)
State daily needs of water in terms of m3
If want to ensure the Required Daily Output of water is supplied even during months with least Sun (i.e. winter or rainy seasons) choose the option ‘Sizing for month with least output’. Otherwise choose ‘Average month’
If you have made a pumping test, introduce here the Safe Yield of the borehole (the maximum amount of water that can be pumped without drying the borehole).

## Slide 5: In case Total Dynamic Head is not known, tick on Pipe length and fill the 3 boxes to the best of your knowledge.
Vertical height from the dynamic water level to the highest point of delivery (not to be mistaken with static water level).
Length of pipe from pump outlet to pump to inlet of tank.
To fill Pipe Type, click on ‘+’, then choose from the displayed ‘Pipe type Menu’ the closest definition to your pipe. In case of doubt, choose the worst case scenario (‘steel, slightly rusty and incrusted’ with Pipe roughness of 0.400).

## Slide 6: Click ‘Calculate’ and see whther your water needs are covered.
Daily water pumped in an average day during the year
62m3/day during December, which is the month with least output for our location. As it is higher than the Daily Required Output introduced (60m3/day), it means this system will provide all the water needed all the year round.
This is an example of m3 pumped per hour in an average day. Pump will start running at 9:00h and will pump 8.1m3/h through 15:00h for 6.8m3/h
Daily water pumped in m3 during April

## Slide 7: Add/ remove solar panels and see how water output change
By clicking report, system characteristics will be shown (pump, number of panels, etc)
By clicking the arrows up/down, number of solar panels can be increased/ decreased and water output will change accordingly. Often several solar panels can be removed without greatly impacting the output of the system whilst saving a significant amount of money.

## Slide 8: By Clicking Report, all data of proposed system will be shown
5 pages showing different system data and drawings
Tick, pump datasheet, module datasheet and then add/remove any accessories that you want to include (water level sensors, water meters etc) before producing the report in .pdf.
You can then generate the pdf report which can be used for to build-up your BOQs and put in Purchase Requests. Solar systems are very specific, so you will generally need to get a waiver for the three quotations if you have used one particular distributor’s calculator.

## Slide 9: Additional resources
COMPASS video tutorials: https://www.lorentz.de/en/partnernet/partner_program/partneracademy/webinar-recordings.html
Tender template for solar pumping tenders: https://www.lorentz.de/en/partnernet/selling/tender.html
pumpScanner remote monitoring App for Android: https://www.lorentz.de/en/partnernet/support/pumpscanner.html
Knowledge Base for tricks and tips about solar pumping: https://www.lorentz.de/en/partnernet/support/knowledge_base.html